## table09_lockouts
1 | ,_T(" | Unconfigured safety data Lockout | ")
2 | ,_T(" | Waiting for safety data verification Lockout | ")
3 | ,_T(" | Internal fault: Hardware fault Hold | ")
4 | ,_T(" | Internal fault: Safety Relay key feedback error Hold | ")
5 | ,_T(" | Internal fault: Unstable power (DCDC) output Hold | ")
6 | ,_T(" | Internal fault: Invalid processor clock Hold | ")
7 | ,_T(" | Internal fault: Safety relay drive error Hold | ")
8 | ,_T(" | Internal fault: Zero crossing not detected Hold | ")
9 | ,_T(" | Internal fault: Flame bias out of range Hold | ")
10 | ,_T(" | Internal fault: Invalid Burner control state Lockout | ")
11 | ,_T(" | Internal fault: Invalid Burner control state flag Lockout | ")
12 | ,_T(" | Internal fault: Safety relay drive cap short Hold | ")
13 | ,_T(" | Internal fault: PII shorted to ILK Hold/Lockout | ")
14 | ,_T(" | Internal fault: HFS shorted to LCI Hold/Lockout | ")
15 | ,_T(" | Internal fault: Safety relay test failed due to feedback ON Lockout | ")
16 | ,_T(" | Internal fault: Safety relay test failed due to safety relay OFF Lockout | ")
17 | ,_T(" | Internal fault: Safety relay test failed due to safety relay not OFF Lockout | ")
18 | ,_T(" | Internal fault: Safety relay test failed due to feedback not ON Lockout | ")
19 | ,_T(" | Internal fault: Safety RAM write Lockout | ")
20 | ,_T(" | Internal fault: Flame ripple and overflow Hold | ")
21 | ,_T(" | Internal fault: Flame number of sample mismatch Hold | ")
22 | ,_T(" | Internal fault: Flame bias out of range Hold | ")
23 | ,_T(" | Internal fault: Bias changed since heating cycle starts Hold | ")
24 | ,_T(" | Internal fault: Spark voltage stuck low or high Hold | ")
25 | ,_T(" | Internal fault: Spark voltage changed too much during flame sensing time Hold | ")
26 | ,_T(" | Internal fault: Static flame ripple Hold | ")
27 | ,_T(" | Internal fault: Flame rod shorted to ground detected Hold | ")
28 | ,_T(" | Internal fault: A/D linearity test fails Hold | ")
29 | ,_T(" | Internal fault: Flame bias cannot be set in range Hold | ")
30 | ,_T(" | Internal fault: Flame bias shorted to adjacent pin Hold | ")
31 | ,_T(" | Internal fault: SLO electronics unknown error Hold | ")
32 | ,_T(" | Internal fault: Safety Key 0 Lockout | ")
33 | ,_T(" | Internal fault: Safety Key 1 Lockout | ")
34 | ,_T(" | Internal fault: Safety Key 2 Lockout | ")
35 | ,_T(" | Internal fault: Safety Key 3 Lockout | ")
36 | ,_T(" | Internal fault: Safety Key 4 Lockout | ")
37 | ,_T(" | Internal fault: Safety Key 5 Lockout | ")
38 | ,_T(" | Internal fault: Safety Key 6 Lockout | ")
39 | ,_T(" | Internal fault: Safety Key 7 Lockout | ")
40 | ,_T(" | Internal fault: Safety Key 8 Lockout | ")
41 | ,_T(" | Internal fault: Safety Key 9 Lockout | ")
42 | ,_T(" | Internal fault: Safety Key 10 Lockout | ")
43 | ,_T(" | Internal fault: Safety Key 11 Lockout | ")
44 | ,_T(" | Internal fault: Safety Key 12 Lockout | ")
45 | ,_T(" | Internal fault: Safety Key 13 Lockout | ")
46 | ,_T(" | Internal fault: Safety Key 14 Lockout | ")
47 | ,_T(" | Flame rod to ground leakage Hold | ")
48 | ,_T(" | Static flame (not flickering) Hold | ")
49 | ,_T(" | 24VAC voltage low/high Hold | ")
50 | ,_T(" | Modulation fault Hold | ")
51 | ,_T(" | Pump fault Hold | ")
52 | ,_T(" | Motor tachometer fault Hold | ")
53 | ,_T(" | AC inputs phase reversed Lockout | ")
54 | ,_T(" | Safety GVT model ID doesn't match application's model ID Lockout | ")
55 | ,_T(" | Application configuration data block CRC errors Lockout | ")
56 | ,_T(" | RESERVED | ")
57 | ,_T(" | RESERVED | ")
58 | ,_T(" | Internal fault: HFS shorted to IAS Lockout | ")
59 | ,_T(" | Internal fault: Mux pin shorted Lockout | ")
60 | ,_T(" | Internal fault: HFS shorted to LFS Lockout | ")
61 | ,_T(" | Anti short cycle Hold | ")
62 | ,_T(" | Fan speed not proved Hold | ")
63 | ,_T(" | LCI OFF Hold | ")
64 | ,_T(" | PII OFF Hold/Lockout | ")
65 | ,_T(" | Interrupted Airflow Switch OFF Hold/Lockout | ")
66 | ,_T(" | Interrupted Airflow Switch ON Hold/Lockout | ")
67 | ,_T(" | ILK OFF Hold/Lockout | ")
68 | ,_T(" | ILK ON Hold/Lockout | ")
69 | ,_T(" | Pilot test hold Hold | ")
70 | ,_T(" | Wait for leakage test completion Hold | ")
71 | ,_T(" | Input power frequency mismatch Lockout | ")
72 | ,_T(" | RESERVED | ")
73 | ,_T(" | RESERVED | ")
74 | ,_T(" | RESERVED | ")
75 | ,_T(" | RESERVED | ")
76 | ,_T(" | RESERVED | ")
77 | ,_T(" | RESERVED | ")
78 | ,_T(" | Demand lost in run Hold | ")
79 | ,_T(" | Outlet high limit Hold/Lockout | ")
80 | ,_T(" | DHW high limit Hold/Lockout | ")
81 | ,_T(" | Delta T inlet/outlet limit Hold/Lockout | ")
82 | ,_T(" | Stack limit Hold/Lockout | ")
83 | ,_T(" | Delta T exchanger/outlet limit Hold/Lockout | ")
84 | ,_T(" | Delta T inlet/exchanger limit Hold/Lockout | ")
85 | ,_T(" | Inlet/outlet inversion limit Hold/Lockout | ")
86 | ,_T(" | Exchanger/outlet inversion limit Hold/Lockout | ")
87 | ,_T(" | Inlet/exchanger inversion limit Hold/Lockout | ")
88 | ,_T(" | Outlet T-rise limit Hold/Lockout | ")
89 | ,_T(" | Exchanger T-rise limit Hold/Lockout | ")
90 | ,_T(" | Heat exchanger high limit Hold/Lockout | ")
91 | ,_T(" | Inlet sensor fault Hold | ")
92 | ,_T(" | Outlet sensor fault Hold | ")
93 | ,_T(" | DHW sensor fault Hold | ")
94 | ,_T(" | S2 (J8-6) sensor fault Hold | ")
95 | ,_T(" | Stack sensor fault Hold | ")
96 | ,_T(" | S5 (J8-11) sensor fault Hold | ")
97 | ,_T(" | Internal fault: A2D mismatch Lockout | ")
98 | ,_T(" | Internal fault: Exceeded VSNSR voltage tolerance Lockout | ")
99 | ,_T(" | Internal fault: Exceeded 28V voltage tolerance Lockout | ")
100 | ,_T(" | Pressure sensor fault Hold | ")
101 | ,_T(" | RESERVED | ")
102 | ,_T(" | RESERVED | ")
103 | ,_T(" | RESERVED | ")
104 | ,_T(" | RESERVED | ")
105 | ,_T(" | Flame detected out of sequence Hold/Lockout | ")
106 | ,_T(" | Flame lost in MFEP Lockout | ")
107 | ,_T(" | Flame lost early in run Lockout | ")
108 | ,_T(" | Flame lost in run Lockout | ")
109 | ,_T(" | Ignition failed Lockout | ")
110 | ,_T(" | Ignition failure occurred Hold | ")
111 | ,_T(" | Flame current lower than WEAK threshold Hold | ")
112 | ,_T(" | Pilot test flame timeout Lockout | ")
113 | ,_T(" | Flame circuit timeout Lockout | ")
114 | ,_T(" | RESERVED | ")
115 | ,_T(" | RESERVED | ")
116 | ,_T(" | RESERVED | ")
117 | ,_T(" | RESERVED | ")
118 | ,_T(" | RESERVED | ")
119 | ,_T(" | RESERVED | ")
120 | ,_T(" | RESERVED | ")
121 | ,_T(" | RESERVED | ")
122 | ,_T(" | Lightoff rate proving failed Lockout | ")
123 | ,_T(" | Purge rate proving failed Lockout | ")
124 | ,_T(" | High fire switch OFF Hold | ")
125 | ,_T(" | High fire switch stuck ON Hold | ")
126 | ,_T(" | Low fire switch OFF Hold | ")
127 | ,_T(" | Low fire switch stuck ON Hold | ")
128 | ,_T(" | Fan speed failed during prepurge Hold/Lockout | ")
129 | ,_T(" | Fan speed failed during preignition Hold/Lockout | ")
130 | ,_T(" | Fan speed failed during ignition Hold/Lockout | ")
131 | ,_T(" | Fan movement detected during standby Hold | ")
132 | ,_T(" | Fan speed failed during run Hold | ")
133 | ,_T(" | RESERVED | ")
134 | ,_T(" | RESERVED | ")
135 | ,_T(" | RESERVED | ")
136 | ,_T(" | Interrupted Airflow Switch failed to close Hold | ")
137 | ,_T(" | ILK failed to close Hold | ")
138 | ,_T(" | RESERVED | ")
139 | ,_T(" | RESERVED | ")
140 | ,_T(" | RESERVED | ")
141 | ,_T(" | RESERVED | ")
142 | ,_T(" | RESERVED | ")
143 | ,_T(" | Internal fault: Flame bias out of range 1 Lockout | ")
144 | ,_T(" | Internal fault: Flame bias out of range 2 Lockout | ")
145 | ,_T(" | Internal fault: Flame bias out of range 3 Lockout | ")
146 | ,_T(" | Internal fault: Flame bias out of range 4 Lockout | ")
147 | ,_T(" | Internal fault: Flame bias out of range 5 Lockout | ")
148 | ,_T(" | Internal fault: Flame bias out of range 6 Lockout | ")
149 | ,_T(" | Flame detected Hold/Lockout | ")
150 | ,_T(" | Flame not detected Hold | ")
151 | ,_T(" | High fire switch ON Hold/Lockout | ")
152 | ,_T(" | Combustion pressure ON Hold/Lockout | ")
153 | ,_T(" | Combustion pressure OFF Hold/Lockout | ")
154 | ,_T(" | Purge fan switch ON Hold/Lockout | ")
155 | ,_T(" | Purge fan switch OFF Hold/Lockout | ")
156 | ,_T(" | Combustion pressure and Flame ON Hold/Lockout | ")
157 | ,_T(" | Combustion pressure and Flame OFF Lockout | ")
158 | ,_T(" | Main valve ON Lockout | ")
159 | ,_T(" | Main valve OFF Lockout | ")
160 | ,_T(" | Ignition ON Lockout | ")
161 | ,_T(" | Ignition OFF Lockout | ")
162 | ,_T(" | Pilot valve ON Lockout | ")
163 | ,_T(" | Pilot valve OFF Lockout | ")
164 | ,_T(" | Block intake ON Lockout | ")
165 | ,_T(" | Block intake OFF Lockout | ")
166 | ,_T(" | RESERVED | ")
167 | ,_T(" | RESERVED | ")
168 | ,_T(" | RESERVED | ")
169 | ,_T(" | RESERVED | ")
170 | ,_T(" | RESERVED | ")
171 | ,_T(" | RESERVED | ")
172 | ,_T(" | Main relay feedback incorrect Lockout | ")
173 | ,_T(" | Pilot relay feedback incorrect Lockout | ")
174 | ,_T(" | Safety relay feedback incorrect Lockout | ")
175 | ,_T(" | Safety relay open Lockout | ")
176 | ,_T(" | Main relay ON at safe start check Lockout | ")
177 | ,_T(" | Pilot relay ON at safe start check Lockout | ")
178 | ,_T(" | Safety relay ON at safe start check Lockout | ")
179 | ,_T(" | RESERVED | ")
180 | ,_T(" | RESERVED | ")
181 | ,_T(" | RESERVED | ")
182 | ,_T(" | RESERVED | ")
183 | ,_T(" | RESERVED | ")
184 | ,_T(" | Invalid BLOWER/HSI output setting Lockout | ")
185 | ,_T(" | Invalid Delta T limit enable setting Lockout | ")
186 | ,_T(" | Invalid Delta T limit response setting Lockout | ")
187 | ,_T(" | Invalid DHW high limit enable setting Lockout | ")
188 | ,_T(" | Invalid DHW high limit response setting Lockout | ")
189 | ,_T(" | Invalid Flame sensor type setting Lockout | ")
190 | ,_T(" | Invalid interrupted air switch enable setting Lockout | ")
191 | ,_T(" | Invalid interrupted air switch start check enable setting Lockout | ")
192 | ,_T(" | Invalid Igniter on during setting Lockout | ")
193 | ,_T(" | Invalid Ignite failure delay setting Lockout | ")
194 | ,_T(" | Invalid Ignite failure response setting Lockout | ")
195 | ,_T(" | Invalid Ignite failure retries setting Lockout | ")
196 | ,_T(" | Invalid Ignition source setting Lockout | ")
197 | ,_T(" | Invalid Interlock open response setting Lockout | ")
198 | ,_T(" | Invalid Interlock start check setting Lockout | ")
199 | ,_T(" | Invalid LCI enable setting Lockout | ")
200 | ,_T(" | Invalid lightoff rate setting Lockout | ")
201 | ,_T(" | Invalid Lightoff rate proving setting Lockout | ")
202 | ,_T(" | Invalid Main Flame Establishing Period time setting Lockout | ")
203 | ,_T(" | Invalid MFEP flame failure response setting Lockout | ")
204 | ,_T(" | Invalid NTC sensor type setting Lockout | ")
205 | ,_T(" | Invalid Outlet high limit response setting Lockout | ")
206 | ,_T(" | Invalid Pilot Flame Establishing Period setting Lockout | ")
207 | ,_T(" | Invalid PII enable setting Lockout | ")
208 | ,_T(" | Invalid pilot test hold setting Lockout | ")
209 | ,_T(" | Invalid Pilot type setting Lockout | ")
210 | ,_T(" | Invalid Postpurge time setting Lockout | ")
211 | ,_T(" | Invalid Power up with lockout setting Lockout | ")
212 | ,_T(" | Invalid Preignition time setting Lockout | ")
213 | ,_T(" | Invalid Prepurge rate setting Lockout | ")
214 | ,_T(" | Invalid Prepurge time setting Lockout | ")
215 | ,_T(" | Invalid Purge rate proving setting Lockout | ")
216 | ,_T(" | Invalid Run flame failure response setting Lockout | ")
217 | ,_T(" | Invalid Run stabilization time setting Lockout | ")
218 | ,_T(" | Invalid Stack limit enable setting Lockout | ")
219 | ,_T(" | Invalid Stack limit response setting Lockout | ")
220 | ,_T(" | Unconfigured Delta T limit setpoint setting Lockout | ")
221 | ,_T(" | Unconfigured DHW high limit setpoint setting Lockout | ")
222 | ,_T(" | Unconfigured Outlet high limit setpoint setting Lockout | ")
223 | ,_T(" | Unconfigured Stack limit setpoint setting Lockout | ")
224 | ,_T(" | Invalid DHW demand source setting Lockout | ")
225 | ,_T(" | Invalid Flame threshold setting Lockout | ")
226 | ,_T(" | Invalid Outlet high limit setpoint setting Lockout | ")
227 | ,_T(" | Invalid DHW high limit setpoint setting Lockout | ")
228 | ,_T(" | Invalid Stack limit setpoint setting Lockout | ")
229 | ,_T(" | Invalid Modulation output setting Lockout | ")
230 | ,_T(" | Invalid CH demand source setting Lockout | ")
231 | ,_T(" | Invalid Delta T limit delay setting Lockout | ")
232 | ,_T(" | Invalid Pressure sensor type setting Lockout | ")
233 | ,_T(" | Invalid IAS closed response setting Lockout | ")
234 | ,_T(" | Invalid Outlet high limit enable setting Lockout | ")
235 | ,_T(" | Invalid Outlet connector type setting Lockout | ")
236 | ,_T(" | Invalid Inlet connector type setting Lockout | ")
237 | ,_T(" | Invalid DHW connector type setting Lockout | ")
238 | ,_T(" | Invalid Stack connector type setting Lockout | ")
239 | ,_T(" | Invalid S2 (J8-6) connector type setting Lockout | ")
240 | ,_T(" | Invalid S5 (J8-11) connector type setting Lockout | ")
241 | ,_T(" | Exchanger sensor not allowed with stack connector setting Lockout | ")
242 | ,_T(" | Invalid DHW auto detect configuration Lockout | ")
243 | ,_T(" | Invalid UV with spark interference not compatible with Ignitor on throughout PFEP Lockout | ")
244 | ,_T(" | Internal fault: Safety relay test invalid state Lockout | ")
245 | ,_T(" | Invalid Outlet connector type setting for Trise Lockout | ")
246 | ,_T(" | 4-20mA cannot be used for both modulation and setpoint control Lockout | ")
247 | ,_T(" | Invalid ILK bounce detection enable Lockout | ")
248 | ,_T(" | Invalid forced recycle interval Lockout | ")
249 | ,_T(" | STAT cannot be demand source when Remote Stat is enabled Lockout | ")
250 | ,_T(" | Invalid Fan speed error response Lockout | ")
251 | ,_T(" | Lead drop-stage on error setting does not match drop method configuration Lockout | ")
252 | ,_T(" | Invalid Line frequency setting Lockout | ")
253 | ,_T(" | RESERVED | ")
254 | ,_T(" | RESERVED | ")
255 | ,_T(" | RESERVED | ")